## Sheet1 (hidden)
01301100 | 10301100 | 0 | 0001 | 0011 | 0000 | 0001 | 0001 | 0000 | 0000
01301D00 | 10301D00 | 0 | 0001 | 0011 | 0000 | 0001 | 1101 | 0000 | 0000
01901100 | 10901100 | 0 | 0001 | 1001 | 0000 | 0001 | 0001 | 0000 | 0000
|  |  |  | 0101 | 0000
01901200 | 10901200 | 0 | 0001 | 1001 | 0000 | 0001 | 0010 | 0000 | 0000
|  |  |  | 0101 | 0000
0D202100 | 1C202100 | 0 | 1101 | 0010 | 0000 | 0010 | 0001 | 0000 | 0000
0D202F00 | 1C202F00 | 0 | 1101 | 0010 | 0000 | 0010 | 1111 | 0000 | 0000
0D203100 | 1C203100 | 0 | 1101 | 0010 | 0000 | 0011 | 0001 | 0000 | 0000
11204100 | 10204100 | 1 | 0001 | 0010 | 0000 | 0100 | 0001 | 0000 | 0000
11204F00 | 10204F00 | 1 | 0001 | 0010 | 0000 | 0100 | 1111 | 0000 | 0000
| 5 |  |  |  | 0000 | 0101
15208100 | 14208100 | 1 | 0101 | 0010 | 0000 | 1000 | 0001 | 0000 | 0000
| 9 |  |  |  | 0000 | 1001
15208F00 | 14208F00 | 1 | 0101 | 0010 | 0000 | 1000 | 1111 | 0000 | 0000
0001
0011
0CF20101 | 1CF20101 | 0 | 1100 | 1111 | 0010 | 0000 | 0001 | 0000 | 0001
0CF20201 | 1CF20201 | 0 | 1100 | 1111 | 0010 | 0000 | 0010 | 0000 | 0001
待屏蔽 | B |  |  | 0111
080a0aff | 180a0aff | 0 | 1000 | 0000 | 1010 | 0000 | 1010 | 1111 | 1111
080a0bff | 180a0bff | 0 | 1000 | 0000 | 1010 | 0000 | 1011 | 1111 | 1111
080a05ff | 180a05ff | 0 | 1000 | 0000 | 1010 | 0000 | 0101 | 1111 | 1111
0CF20301 | 1CF20301 | 0 | 1100 | 1111 | 0010 | 0000 | 0011 | 0000 | 0001
0CF20401 | 1CF20401 | 0 | 1100 | 1111 | 0010 | 0000 | 0100 | 0000 | 0001
08f50A01 | 18f50A01 | 0 | 1000 | 1111 | 0101 | 0000 | 1010 | 0000 | 0001
04F10B00 | 14F10B00 | 0 | 0100 | 1111 | 0001 | 0000 | 1011 | 0000 | 0000
0CF20801 | 1CF20801 | 0 | 1100 | 1111 | 0010 | 0000 | 1000 | 0000 | 0001
08f50B01 | 18f50B01 | 0 | 1000 | 1111 | 0101 | 0000 | 1011 | 0000 | 0001
04F10C00 | 14F10C00 | 0 | 0100 | 1111 | 0001 | 0000 | 1100 | 0000 | 0000
0CF20901 | 1CF20901 | 0 | 1100 | 1111 | 0010 | 0000 | 1001 | 0000 | 0001
| D | 9 | F | F | 1101 | F | F | F | F | 0x9FFDFFFF
|  | 9 | F | F | D | 3 | F | F | F | 0x9FFD3FFF
|  | 9 | F | F | D | 0 | F | F | F | 0x9FFD1FFF
|  | 9 | F | F | F | 9 | F | 0 | F | 0x9FDF9FFF
|  | 9 | F | F | F | F | 3 | F | F | 0x9FFFF3FF
| 00301100 | 0000 | 0001 | 0001 | 1010
| 00301D00 | 0000 | 0001 | 1101
| 00901100 | 0000 | 0001 | 0001 | [8 empty] | 00301100 |  | 00301100
| 00901200 | 0000 | 0001 | 0010 | [8 empty] | 00301D00 |  | 00301D00
| 0C202100 | 0000 | 0010 | 0001 | [8 empty] | 00901100 | 00901100 | 00901100
| 0C202F00 | 0000 | 0010 | 1111
| 0C203100 | 0000 | 0011 | 0001 | [8 empty] | 00901200 | 00901200 | 00901200
| 10204100 | 0000 | 0100 | 0001 | [7 empty] | 00301100
| 10204F00 | 0000 | 0100 | 1111 | [7 empty] | 00301D00 | 0C202100 |  | 0C202100
| 14208100 | 0000 | 1000 | 0001 | [7 empty] | 00901100 | 0C202F00 |  | 0C202F00
| 14208F00 | 0000 | 1000 | 1111 | [7 empty] | 00901200 | 0C203100 |  | 0C203100
| ##DFF## | [9 empty] | 0x9FFD0FFF | 0x9FFD1FFF | 0x9FFD3FFF | 0x9FDF9FFF
| 08f50A01 | 0101 | 0000 | 1010 | [6 empty] | 08f50A01 | 08f50A01 | 08f50A01 | 080a0aff | 08f50A01
| 04F10B00 | 0001 | 0000 | 1011 | [6 empty] | 04F10B00 | 04F10B00 | 04F10B00 | 080a0bff | 04F10B00
| 08f50B01 | 0101 | 0000 | 1011 | [6 empty] | 08f50B01 | 08f50B01 | 08f50B01 | 080a05ff | 08f50B01
| 04F10C00 | 0001 | 0000 | 1100 | [6 empty] | 04F10C00 | 04F10C00 | 04F10C00 |  | 04F10C00
| ##9FF## | 1001
| ##2FF## | 10
| ##AFF## | 1010
0x9FFFF3FF

## Charger ModbusRtu (ID == 4)
Register Address（decimalism） |  | Register Type | Register Name |  | Effective Range | note
Charger Control Message
10001 | 23421 | RO | The type of machine | PC1600
10002 | 23422 | WR | Serial number High
10003 | 23423 | WR | Serial number Low
10004 | 23424 | RO | Hardware version | 1.0.00
10005 | 23425 | RO | Software version | 1.0.00
10006 | 23426 | WR | PV voltage calibration coefficient | 16384
10007 | 23427 | WR | Battery voltage calibration coefficient | 16384
10008 | 23430 | WR | Charger current calibration coefficient | 16384
10009-10100 | #VALUE! | WR | reserved | reserved
10101 | 23565 | WR | charger work enable | 0：OFF 1：ON | effective range：0,1 the default value is 1；
10102 | 23566 | WR | Absorb voltage | 0.1V | 480~540(48.0-54.0)V the default value is 50.0V
10103 | 23567 | WR | Refloat voltage | 0.1V | 510~580(51.0-58.0)V the default value is 54.8V
10104 | 23570 | WR | Float voltage | 0.1V | 530~580(53.0-58.0)V the default value is 57.2V
10105 | 23571 | WR | Battery low voltage | 0.1V | 340~440(34.0-44.0)V the default value is 34.0V
10106 | 23572 | WR | reserved
10107 | 23573 | WR | Battery High voltage | 0.1V | 580~600(58.0-60.0)V the default value is 60.0V
10108 | 23574 | WR | Max charger current | 0.1A | 0.1A effective range：(0-80)A
10109 | 23575 | WR | Absorb charger current | 0.1A | 0.1A effective range：(0-80)A
10110 | 23576 | WR | Battery type | 0: no choose 1：lead acid battery 2：lithium battery | the default value is 0；effective range：0,2
10111 | 23577 | WR | Battery AH | 1AH | effective range：(0-900)AH the default value is 100AH
10112 | 23600 | WR | Remove the accumulated data | 0：No remove the accumulated data 1：Remove the accumulated data | the default value is 0；effective range：0,1
Register Address（decimalism） |  | Register Type | Register Name | Physical Unit | Effective Range | note
Charger Display Message
15201 | 35541 | RO | Charger workstate | 0：Initialization mode 1：Selftest Mode 2: Work Mode 3：Stop Mode
15202 | 35542 | RO | Mppt state | 0：Stop 1：MPPT 2: Current limiting
15203 | 35543 | RO | charging state | 0：Stop 1：Absorb charge 2: Float charge
15204 | 35544 | RO | reserved
15205 | 35545 | RO | PV voltage | 0.1V | (0.0-150.0)V
15206 | 35546 | RO | Battery voltage | 0.1V | (0.0-80.0)V
15207 | 35547 | RO | Charger current | 0.1A | (0.0-90.0)A
15208 | 35550 | RO | Charger power | 1W | (0-5000)W
15209 | 35551 | RO | Radiator temperature | 1℃ | (-40-150)℃
15210 | 35552 | RO | External temperature | 1℃ | (-40-150)℃
15211 | 35553 | RO | Battery Relay |  | 0: Disconnect 1:Connect
15212 | 35554 | RO | PV Relay |  | 0: Disconnect 1:Connect
15213 | 35555 | RO | Error message | Refer to frame Charger Error message 1
15214 | 35556 | RO | Warning message | Refer to frame Charger Warning message 1
15215 | 35557 | RO | BattVol Grade | 1V
15216 | 35560 | RO | Rated Current | 0.1A
15217 | 35561 | RO | Accumulated power high | 1000KWH
15218 | 35562 | RO | Accumulated power low | 0.1KWH
15219 | 35563 | RO | Accumulated day | 1day
15220 | 35564 | RO | Accumulated hour | 1hour
15221 | 35565 | RO | Accumulated minute | 1minute

## Inverter modbusRTU (ID == 4)
Register Address（decimalism） |  | Register Type | Register Name | Physical Unit | Effective Range | note
Inverter Control Message
20001 | 47041 | RO | The type of machine | PH1000/PH3000/PH1800
20002 | 47042 | RW | Serial number High
20003 | 47043 | RW | Serial number Low
20004 | 47044 | RO | Hardware version | 1.00.00
20005 | 47045 | RO | Software version | 1.00.00
20006-20008 | #VALUE! | RW | reserved | reserved
20009 | 47051 | RW | Battery voltage calibration coefficient | 16384
20010 | 47052 | RW | Inverter voltage calibration coefficient | 16384
20011 | 47053 | RW | Grid voltage calibration coefficient | 16384
20012 | 47054 | RW | Bus voltage calibration coefficient | 16384
20013 | 47055 | RW | Control Current calibration coefficient | 16384
20014 | 47056 | RW | Inverter Current calibration coefficient | 16384
20015 | 47057 | RW | Grid Current calibration coefficient | 16384
20016 | 47060 | RW | Load Current calibration coefficient | 16384
20017-20100 |  | RW | reserved | reserved
20101 | 47205 | RW | Inverter offgrid work enable | 0：OFF 1：ON | effective range：0,1 the default value is 1； | 1:Turn on the inverter output when the grid is off. 0:Shut down the inverter output when the grid is off.
20102 | 47206 | RW | Inverter output voltage Set | 220.0V-240.0V | (2200-2400) | Set the output voltage amplitude.
20103 | 47207 | RW | Inverter output frequency Set | 50.00Hz/60.00Hz | 5000/6000 | Set the output frequency.
20104 | 47210 | RW | Inverter search mode enable | 0：OFF 1：ON | effective range：0,1 the default value is 0； | 0:If disabled, no matter connect load is low or high, the on/off status of inverter output will not be effected. 1:If enable, the inverter begins search mode if the AC load connected is pretty low or not detected. The inverter’s “search” mode reduces stand-by energy consumption during no-load conditions.
20105 | 47211 | RW | Inverter ongrid work enable | 0：OFF 1：ON | effective range：0,1 the default value is 1； | 1:Enable the inverter connect to an AC input source. 0:Disable the inverter connect to an AC input source.
20106 | 47212 | RW | Inverter charger from grid enable | 0：OFF 1：ON | effective range：0,1 the default value is 1； | 1:Enable grid charge 0:Disable grid charge
20107 | 47213 | RW | Inverter discharger enable | 0：OFF 1：ON | effective range：0,1 the default value is 1； | 1:Enable Inveter discharging from battery when the Inverter is connnectted to Grid 0:Disable Inveter discharging from battery when the Inverter is connnectted to Grid
20108 | 47214 | RW | Inverter discharger to grid enable | 0：OFF 1：ON | effective range：0,1 the default value is 1； | 1:Enable Inveter discharging from battery to grid when the Inverter is connnectted to Grid 0:Disable Inveter discharging from battery to grid when the Inverter is connnectted to Grid
20109 | 47215 | RW | Energy use mode | 0:PL ; 1:FL; 2:FS; 3:UPS; 4: PO(Old) 0:SUB;1SBU;3:UTI;(New) |  | refer to user's manual
20110 | 47216 | RW | Time mode use enable | 0：disable 1：enable |  | 0: Disable 1: Enable
20111 | 47217 | RW | Grid protect standard | 0：VDE4105; 1：UPS ; 2：home |  | refer to user's manual
20112 | 47220 | RW | SolarUse Aim | 0:LBU 1:BLU(defalut)
20113 | 47221 | RW | Inverter max discharger current | 0.1A（AC） | 1.0A-17.4A（10-174） | Set the max discharging current from Inverter
20114 | 47222 | RW | Inverter max charger current | 0.1A （AC） | 1.0A-17.4A（10-174） | Set the max charging current from Inverter
20115 | 47223 | RW | Grid max output current | 0.1A（AC） | 0A-26.0A（0-260） | Set the max selling current from Inverter to grid
20116 | 47224 | RW | Grid max input current | 0.1A（AC） | 0A-26.0A（0-260） | Set the max Input current from grid
20117 | 47225 | RW | start charger voltage point | 0.1V | 450~540(45.0-54.0)V the default value is 48.0V | refer to user's manual
20118 | 47226 | RW | normal voltage point | 0.1V | 480~550(48.0-55.0)V the default value is 53.0V | refer to user's manual
20119 | 47227 | RW | start sell voltage point | 0.1V | 500~540(50.0-58.0)V the default value is 54.0V | refer to user's manual
20120 | 47230 | RW | Batt low protection mode | 0:usually_defined 1:user_defined |  | refer to user's manual
20121 | 47231 | RW | reserved | reserved
20122 | 47232 | RW | reserved | reserved
20123 | 47233 | RW | reserved | reserved
20124 | 47234 | RW | reserved | reserved
20125 | 47235 | RW | Grid max charger current set | 0.1A(DC) | 10~800(1.0-80.0)A the default value is 60.0A
20126 | 47236 | RW | Absorb charger current set | 0.1A(DC) | 10~300(1.0-30.0)A the default value is 10.0A
20127 | 47237 | RW | Battery low voltage | 0.1V | 400~440(40.0-44.0)V the default value is 42.0V
20128 | 47240 | RW | Battery high voltage | 0.1V | 580~600(58.0-60.0)V the default value is 60.0V
20129 | 47241 | RW | Battery type | 0: no choose 1:Use_defined battery 2:lithium battery 3:Sealed_lead battery 4:AGM battery (default) 5:GEL battery 6:Flooded battery | the default value is 4; effective range：0,6
20130 | 47242 | RW | Battery AH | 1AH | effective range：(0-900)AH the default value is 100AH
20131 | 47243 | RW | battery low return voltage | 0.1V | 400~500(40.0-50.0)V the default value is 44.0V
20132 | 47244 | RW | Max Combine charger current | 0.1A(DC) | 10~1400(1.0-140.0)A the default value is 60.0A
20133 | 47245 | RW | Charger Start Time（Hour） | 1h
20134 | 47246 | RW | Charger Start Time（Minutes） | 1min
20135 | 47247 | RW | Charger End Time（Hour） | 1h
20136 | 47250 | RW | Charger End Time（Minutes） | 1min
20137 | 47251 | RW | Discharger Start Time（Hour） | 1h
20138 | 47252 | RW | Discharger Start Time（Minutes） | 1min
20139 | 47253 | RW | Discharger End Time（Hour） | 1h
20140 | 47254 | RW | Discharger End Time（Minutes） | 1min
20142 | 47256 | RW | System setting |  | refer to the frame System setting bit
20143 | 47257 | RW | Charger source priority | 0:Soalr first 2:Solar and Utility(default) 3:Only Solar
20161 | 47301 | RW | Gridtie Safety type | 0：VDE4105 1：AS4777 2：CEI021 3：user define
20162 | 47302 | RW | Auto Test Start Cmd | 1：Start 0：Stop
20163 | 47303 | RW
20164 | 47304 | RW
20165 | 47305 | RW | Grid LVP Slow Protetion Value | 0.1V | LVP:Low voltage protection
20166 | 47306 | RW | Grid LVP Slow Protetion Time | 10ms
20167 | 47307 | RW | Grid OVP Slow Protetion Value | 0.1V | OVP:Over voltage protection
20168 | 47310 | RW | Grid OVP Slow Protetion Time | 10ms
20169 | 47311 | RW | Grid LVP Fast Protetion Value | 0.1V
20170 | 47312 | RW | Grid LVP Fast Protetion Time | 10ms
20171 | 47313 | RW | Grid OVP Fast Protetion Value | 0.1V
20172 | 47314 | RW | Grid OVP Fast Protetion Time | 10ms
20173 | 47315 | RW | Frequency low Protection Value | 0.01Hz
20174 | 47316 | RW | Frequency low Protection Time | 10ms
20175 | 47317 | RW | Frequency High Protection Value | 0.01Hz
20176 | 47320 | RW | Frequency High Protection Time | 10ms
20177 | 47321 | RW
20178 | 47322 | RW
20179 | 47323 | RW
20180 | 47324 | RW
20181 | 47325 | RW
20182 | 47326 | RW
20183 | 47327 | RW | Reconect Time | 1s
20184 | 47330 | RW
20185 | 47331 | RW | Q-U Characteristic Curve Start point | 0.01v
20186 | 47332 | RW | PF-P Characteristic Curve Power point | 1%
20187 | 47333 | RW | PF-P Characteristic Curve Volt. point | 0.1v
20188 | 47334 | RW | Power recover speed %Pn/min | 1%
20189-20190 | #VALUE! | RW | 保留
20191 | 47337 | RW | Output Q Mode | 0：PF Curv, 1: QU Curv
20192 | 47340 | RW | Active Power Setting | w
20193 | 47341 | RW | Reactive Power Setting | w
20194 | 47342 | RW
20195-20200 | #VALUE! | RW | 保留
20201 | 47351 | RW | Year
20202 | 47352 | RW | Month
20203 | 47353 | RW | Day
20204 | 47354 | RW
20205 | 47355 | RW | Hour
20206 | 47356 | RW | Minutes
20207 | 47357 | RW | Seconds
20208 | 47360 | RW
20209 | 47361 | RW | Force charger enable | 0：Enable 1：Disable
20210 | 47362 | RW | Force discharger enable | 0：Enable 1：Disable
20211 | 47363 | RW
20212 | 47364 | RW
20213 |  | RW | Remove the accumulated data | 0：No remove the accumulated data 1：Remove the accumulated data | the default value is 0; effective range:0,1
20214 |  | RW | Reset the parameter | 0：No effect 1：Action | the default value is 0; effective range:0,1
Register Address（decimalism） |  | Register Type | Register Name | Physical Unit | Effective Range | note
Inverter Display Message
25201 | 61161 | RO | work state | 0:PowerOn 1:SelfTest 2:OffGrid 3:Grid-Tie 4:ByPass 5:Stop
25202 | 61162 | RO | AC voltage grade | 230:230V 120:120V
25203 | 61163 | RO | Rated power | PV1800 VA/PH3000 W
25204 | 61164 | RO | reserved
25205 | 61165 | RO | Battery voltage | 0.1V
25206 | 61166 | RO | Inverter voltage | 0.1V
25207 | 61167 | RO | Grid voltage | 0.1V
25208 | 61170 | RO | BUS voltage | 0.1V
25209 | 61171 | RO | Control current | 0.1A
25210 | 61172 | RO | Inverter current | 0.1A
25211 | 61173 | RO | Grid current | 0.1A
25212 | 61174 | RO | Load current | 0.1A
25213 | 61175 | RO | PInverter | 1W
25214 | 61176 | RO | PGrid | 1W
25215 | 61177 | RO | PLoad | 1W
25216 | 61200 | RO | Load percent | 1% | new
25217 | 61201 | RO | SInverter | 1VA
25218 | 61202 | RO | SGrid | 1VA
25219 | 61203 | RO | Sload | 1VA
25220 | 61204 | RO | reserved
25221 | 61205 | RO | Qinverter | 1var
25222 | 61206 | RO | Qgrid | 1var
25223 | 61207 | RO | Qload | 1var
25224 | 61210 | RO | reserved
25225 | 61211 | RO | Inverter frequency | 0.01Hz
25226 | 61212 | RO | Grid frequency | 0.01Hz
25227 | 61213 | RO | reserved
25228 | 61214 | RO | reserved
25229 | 61215 | RO | Inverter max number
25230 | 61216 | RO | Combine type
25231 | 61217 | RO | Inverter number
25232 | 61220 | RO | reserved
25233 | 61221 | RO | AC radiator temperature | 1℃
25234 | 61222 | RO | Transformer temperature | 1℃
25235 | 61223 | RO | DC radiator temperature | 1℃
25236 | 61224 | RO | reserved
25237 | 61225 | RO | Inverter relay state | 0: Disconnect 1:Connect
25238 | 61226 | RO | Grid relay state | 0: Disconnect 1:Connect
25239 | 61227 | RO | Load relay state | 0: Disconnect 1:Connect
25240 | 61230 | RO | N_Line relay state | 0: Disconnect 1:Connect
25241 | 61231 | RO | DC relay state | 0: Disconnect 1:Connect
25242 | 61232 | RO | Earth relay state | 0: Disconnect 1:Connect
25243 | 61233 | RO | reserved
25244 | 61234 | RO | reserved
25245 | 61235 | RO | Accumulated charger power high | 1000KWH
25246 | 61236 | RO | Accumulated charger power low | 0.1KWH
25247 | 61237 | RO | Accumulated discharger power high | 1000KWH
25248 | 61240 | RO | Accumulated discharger power low | 0.1KWH
25249 | 61241 | RO | Accumulated buy power high | 1000KWH
25250 | 61242 | RO | Accumulated buy power low | 0.1KWH
25251 | 61243 | RO | Accumulated sell power high | 1000KWH
25252 | 61244 | RO | Accumulated sell power low | 0.1KWH
25253 | 61245 | RO | Accumulated load power high | 1000KWH
25254 | 61246 | RO | Accumulated load power low | 0.1KWH
25255 | 61247 | RO | Accumulated self_use power high | 1000KWH
25256 | 61250 | RO | Accumulated self_use power low | 0.1KWH
25257 | 61251 | RO | Accumulated PV_sell power high | 1000KWH
25258 | 61252 | RO | Accumulated PV_sell power low | 0.1KWH
25259 | 61253 | RO | Accumulated grid_charger power high | 1000KWH
25260 | 61254 | RO | Accumulated grid_charger power low | 0.1KWH
25261 | 61255 | RO | Error message 1 |  | Refer to frame Error message 1
25262 | 61256 | RO | Error message 2 |  | Refer to frame Error message 2
25263 | 61257 | RO | Error message 3 |  | Refer to frame Error message 3
25264 | 61260 | RO | reserved
25265 | 61261 | RO | Warning message 1 |  | Refer to frame Warning message 1
25266 | 61262 | RO | Warning message 2 |  | Refer to frame Warning message 2
25267 | 61263 | RO | reserved
25268 | 61264 | RO | reserved
25269 | 61265 | RO | Serial number High
25270 | 61266 | RO | Serial number Low
25271 | 61267 | RO | Hardware version | 1.00.00
25272 | 61270 | RO | Software version | 1.00.00
25273 | 61271 | RO | Batt power | W
25274 | 61272 | RO | Batt current | A
System setting bit
Bit |  | meaning
0 |  | OverLoadRestartForbid
1 |  | OverTempRestartForbid
2 |  | OverLoadBypassForbid
3 |  | AutoTurnPageFlagForbid
4 |  | GridBuzzEnable(only use by PV1800)
5 |  | BuzzForbide(only use by PV1800)
6 |  | LcdLightEnable
7 |  | RecordFaultForbid
8 |  | reserved
9 |  | reserved
10 |  | reserved
11 |  | reserved
12 |  | reserved
13 |  | reserved
14 |  | reserved
15 |  | reserved

## Inverter Alarm
Inverter error message 1 |  |  | Inverter warning message 1
Bit | meaning | description | Inverter Warning message 1 | meaning | description
0 | Fan is locked when inverter is off | 0：normal 1：fault | 0 | Fan is locked when inverter is on. | 0：normal 1：fault
1 | Inverter transformer over temperature | 0：normal 1：fault | 1 | Fan2 is locked when inverter is on. | 0：normal 1：fault
2 | battery voltage is too high | 0：normal 1：fault | 2 | Battery is over-charged. | 0：normal 1：fault
3 | battery voltage is too low | 0：normal 1：fault | 3 | Low battery | 0：normal 1：fault
4 | Output short circuited | 0：normal 1：fault | 4 | Overload | 0：normal 1：fault
5 | Inverter output voltage is high | 0：normal 1：fault | 5 | Output power derating | 0：normal 1：fault
6 | Overload time out | 0：normal 1：fault | 6 | Solar charger stops due to low battery. | 0：normal 1：fault
7 | Inverter bus voltage is too high | 0：normal 1：fault | 7 | Solar charger stops due to high PV voltage. | 0：normal 1：fault
8 | Bus soft start failed | 0：normal 1：fault | 8 | Solar charger stops due to over load. | 0：normal 1：fault
9 | Main relay failed | 0：normal 1：fault | 9 | Solar charger over temperature | 0：normal 1：fault
10 | Inverter output voltage sensor error | 0：normal 1：fault | 10 | PV charger communication error | 0：normal 1：fault
11 | Inverter grid voltage sensor error | 0：normal 1：fault | 11 | reserved | 0：normal 1：fault
12 | Inverter output current sensor error | 0：normal 1：fault | 12 | reserved | 0：normal 1：fault
13 | Inverter grid current sensor error | 0：normal 1：fault | 13 | reserved | 0：normal 1：fault
14 | Inverter load current sensor error | 0：normal 1：fault | 14 | reserved | 0：normal 1：fault
15 | Inverter grid over current error | 0：normal 1：fault | 15 | reserved | 0：normal 1：fault
Inverter error message 2 |  |  | Inverter warning message 2
Bit | meaning | description | Inverter Warning message 2 | meaning | description
0 | Inverter radiator over temperature | 0：normal 1：fault | 0 | reserved | 0：normal 1：fault
1 | Solar charger battery voltage class error | 0：normal 1：fault | 1 | reserved | 0：normal 1：fault
2 | Solar charger current sensor error | 0：normal 1：fault | 2 | reserved | 0：normal 1：fault
3 | Solar charger current is uncontrollable | 0：normal 1：fault | 3 | reserved | 0：normal 1：fault
4 | Inverter grid voltage is low | 0：normal 1：fault | 4 | reserved | 0：normal 1：fault
5 | Inverter grid voltage is high | 0：normal 1：fault | 5 | reserved | 0：normal 1：fault
6 | Inverter grid under frequency | 0：normal 1：fault | 6 | reserved | 0：normal 1：fault
7 | Inverter grid over frequency | 0：normal 1：fault | 7 | reserved | 0：normal 1：fault
8 | Inverter over current protection error | 0：normal 1：fault | 8 | reserved | 0：normal 1：fault
9 | Inverter bus voltage is too low | 0：normal 1：fault | 9 | reserved | 0：normal 1：fault
10 | Inverter soft start failed | 0：normal 1：fault | 10 | reserved | 0：normal 1：fault
11 | Over DC voltage in AC output | 0：normal 1：fault | 11 | reserved | 0：normal 1：fault
12 | Battery connection is open | 0：normal 1：fault | 12 | reserved | 0：normal 1：fault
13 | Inverter control current sensor error | 0：normal 1：fault | 13 | reserved | 0：normal 1：fault
14 | Inverter output voltage is too low | 0：normal 1：fault | 14 | reserved | 0：normal 1：fault
15 | reserved | 0：normal 1：fault | 15 | reserved | 0：normal 1：fault

## Charger Alarm
Charger error message 1 |  |  | Charger Warning message 1
Bit | meaning | description | Charger Warning message 1 | meaning | description
0 | Hardware protection | 0：normal 1：fault | 0 | Fan Error | 0：normal 1：fault
1 | Over current | 0：normal 1：fault | 1 | reserved | 0：normal 1：fault
2 | Current sensor error | 0：normal 1：fault | 2 | reserved | 0：normal 1：fault
3 | Over temperature | 0：normal 1：fault | 3 | reserved | 0：normal 1：fault
4 | PV voltage is too high | 0：normal 1：fault | 4 | reserved | 0：normal 1：fault
5 | PV voltage is too low | 0：normal 1：fault | 5 | reserved | 0：normal 1：fault
6 | Battery voltage is too high | 0：normal 1：fault | 6 | reserved | 0：normal 1：fault
7 | Battery voltage is too Low | 0：normal 1：fault | 7 | reserved | 0：normal 1：fault
8 | Current is uncontrollable | 0：normal 1：fault | 8 | reserved | 0：normal 1：fault
9 | Parameter error | 0：normal 1：fault | 9 | reserved | 0：normal 1：fault
10 | reserved | 0：normal 1：fault | 10 | reserved | 0：normal 1：fault
11 | reserved | 0：normal 1：fault | 11 | reserved | 0：normal 1：fault
12 | reserved | 0：normal 1：fault | 12 | reserved | 0：normal 1：fault
13 | reserved | 0：normal 1：fault | 13 | reserved | 0：normal 1：fault
14 | reserved | 0：normal 1：fault | 14 | reserved | 0：normal 1：fault
15 | reserved | 0：normal 1：fault | 15 | reserved | 0：normal 1：fault